- SSBF-54* – Barrier Free, recessed, cleanroom, wall mounted combination eye/face wash and shower safety station with wall mounted exposed shower head, patented stainless steel shower-actuating arm, swing-down stainless steel combination eye/face wash drain pan, and 1” IPS stainless steel daylight drain. Unit construction shall be welded 16-gauge type 304 stainless steel with #4 brushed satin finish. Unit shall include stainless steel shower head, internal 20 GPM flow control, supply nipple, escutcheon, chrome-plated brass eye/face wash supply fittings, brass unions, and U.S made full-port brass ball valve for shower. Eye/face wash valve shall be AutoFlow™, plug-type design with PTFE coated O-rings to seal valve orifices, polypropylene FS-Plus™ spray heads with individual 3.2 GPM flow controls and polyurethane filters. Supplied with in-line strainer to protect eye/face wash valve and spray heads from debris in water line. Activate eye/face wash valve by rotating 90° from stored position. Unit is completely sealed and airtight. Covers conceal all openings on front of unit. Supply nipples on inlet and outlet of shower valve are sealed with grommets. All seams in cabinet are fully welded and polished. Unit shall include ANSI compliant sign.

- Performance: Unit complies with ADA requirements for accessibility by handicapped persons. Unit shall be fully factory assembled and hydrostatically tested to meet or exceed ANSI Z358.1 – 2014, and come with a full 2-year warranty.

- Fixture: Guardian GBF2472